## Slide 1
ASCE 7-22 Ch 15 Seismic Design Requirements for Nonbuilding Structures
By Tom Irvine

## Slide 2
Introduction
Structures that are not intended for human occupancy
Tanks (ground-supported, elevated)
Stacks / chimneys
Pipe racks
Towers (telecom, industrial)
Mechanical/equipment frames
Vibrationdata

## Slide 3
Introduction
Traditional building rules (Ch. 12) do not apply directly
Nonbuilding structures are
  Often highly dynamic
  Frequently flexible and lightly damped
Nonbuilding structures often have:
  Different mass/stiffness distributions
  Significant fluid-structure interaction
  Equipment-driven loads
Goal: Provide consistent seismic design framework
Vibrationdata
Big Peach Water Tower, Clanton, GA

## Slide 4
Classification
Supported Nonbuilding Structures
  Supported by buildings
  Example: rooftop equipment frames
Nonbuilding Structures Similar to Buildings
  Act like buildings dynamically
  Example: pipe racks, structural frames
Other Nonbuilding Structures
  Require special procedures
  Tanks, stacks, silos
Vibrationdata
Pipe Rack
Rooftop Equipment
Design path depends on classification:
Use Chapter 12 (ELF / MRSA) if Structure behaves like a building
Use Chapter 15 provisions if: Unique dynamic behavior exists

## Slide 5
Chapter 15 Design Path Flowchart
Does it behave like a building?
  Use Chapter 12 (ELF / MRSA)
Is it supported by a building?
  Use Chapter 13 + 15 interface
Otherwise:
  Use Chapter 15 provisions
Then:
  Identify applicable standard (AWWA, API, etc.)
  Determine R, Cd, Ω₀ source
Vibrationdata

## Slide 6
Dynamic Behavior Comparison
Vibrationdata
Feature | Buildings | Nonbuilding Structures
Damping | Moderate | Often low
Modes | 1st mode dominant | Multi-mode important
Mass distribution | Uniform | Concentrated / irregular
Special effects | Rare | Sloshing, appendages

## Slide 7
Design Approach
Determine:
  Seismic Design Category (SDC)
  Risk Category
Select:
  Analysis method
  Structural system
Apply:
  Appropriate R, Cd, Ω₀ factors
  Review Relevant Slides from Previous Units
Vibrationdata

## Slide 8
Vibrationdata
Seismic Hazard Map
SDC | Detailing Level
A–B | Minimal
C | Moderate
D–F | Special (strict)

## Slide 9
Vibrationdata
Risk Categories
Risk Category | Meaning | Typical Examples | Importance Factor Ie | Typical Interstory Lateral Drift Limit
I | Low risk to life if failure occurs | Barns, sheds, low-occupancy storage | 1.00 | 0.020 h
II | Ordinary risk structures (most buildings) | Homes, offices, retail | 1.00 | 0.020 h
III | Substantial hazard to life & community | Schools, assembly buildings, prisons | 1.25 | 0.015 h
IV | Essential facilities — must remain operational | Hospitals, fire/police stations | 1.50 | 0.010 h
Olive View Hospital, Los Angeles, San Fernando earthquake 1971
h is the story height measured between floor levels

## Slide 10
Vibrationdata
Three Seismic Modification Coefficients
Base shear
Lateral Force Amplification for specific elements that remain elastic
Factor | Used For | Physical Meaning | Notes
Response (R) | Reduces base shear | Expected ductility | Global energy dissipation assumption
Overstrength (Ω₀) | Amplifies forces locally | Hidden overstrength | Protects brittle/local elements
Deflection (Cd) | Amplifies drift | Inelastic deformation | Reconstructs actual deformation

## Slide 11
Vibrationdata
Response Modification Factor R “Credit for Ductility”
It accounts for:
  Ductility
  Overstrength
  Redundancy
  Energy dissipation capacity
Larger R → smaller base shear
Smaller R → larger base shear
Higher ductility systems permit higher R
Large R assumes the structure can:
  Yield
  Form plastic hinges
  Dissipate energy
  Redistribute forces
Large R trades strength for ductility and allows for inelastic deformation

## Slide 12
Vibrationdata
Overstrength Factor Ω₀
Reflects reserve strength + system redundancy
Lateral Force Amplification for specific elements that remain elastic
Overstrength Factor Use
  The overstrength factor ensures that critical elements, like foundations and columns, are designed to handle amplified forces
  This way, these parts will survive before the more ductile elements, like beams, which are intended to yield first
Benefits and Trade-Offs
  The overstrength factor:
  Helps prevent sudden brittle failures
  Supports a strong-column/weak-beam design approach improves overall seismic safety

## Slide 13
Typical Values
Vibrationdata
System Type | Response Modification (R) | Deflection Factor ( ) | Overstrength Factor (Ω₀)
Ordinary Moment Frame (OMF) | 3.5 | 3 | 3
Intermediate Moment Frame (IMF) | 4.5 | 4 | 3
Special Moment Frame (SMF) | 8 | 5.5 | 3
Ordinary Braced Frame (OCBF) | 3.25 | 3.25 | 2
Special Concentric Braced Frame (SCBF) | 6 | 5 | 2
Eccentric Braced Frame (EBF) | 8 | 4 | 2.5
Ordinary Shear Wall | 3 | 2.5 | 2.5
Special Reinforced Concrete Shear Wall | 6 | 5 | 2.5
Dual System (SMF + Shear Wall) | 8 | 5.5 | 3
System Type | Response Modification (R) |  | Overstrength Factor (Ω₀)
Ordinary Moment Frame (OMF) | 3.5 | 3 | 3
Intermediate Moment Frame (IMF) | 4.5 | 4 | 3
Special Moment Frame (SMF) | 8 | 5.5 | 3
Ordinary Braced Frame (OCBF) | 3.25 | 3.25 | 2
Special Concentric Braced Frame (SCBF) | 6 | 5 | 2
Eccentric Braced Frame (EBF) | 8 | 4 | 2.5
Ordinary Shear Wall | 3 | 2.5 | 2.5
Special Reinforced Concrete Shear Wall | 6 | 5 | 2.5
Dual System (SMF + Shear Wall) | 8 | 5.5 | 3

## Slide 14
Vibrationdata
Seismic Separation Gap
To prevent pounding (structural collision) between adjacent buildings or different parts of the same building during an earthquake
Pounding can cause localized crushing, shear failure in columns, or even progressive collapse
Minimum Separation Distance ( )
Each building must be set back from the property line by a distance at least equal to its Maximum Displacement (), calculated at each floor level
  : Deflection determined by elastic analysis
  : Deflection Amplification Factor (from Table 12.2-1)
  : Importance Factor
Assessing seismic gap in adjacent RC buildings post Gorkha earthquake in Nepal, Aviral Upadhayay, et al.

## Slide 15
Standards
ASCE 7-22 provides seismic demand
The following standards give resistance design details:
  ACI 350 / 371 (tanks)
  AWWA D100 (steel tanks)
  API 650 Appendix E (storage tanks)
  ASME / industry standards
Vibrationdata

## Slide 16
Seismic Forces
Base shear similar to buildings:
Depends on:
  SDS, SD1
  Period
  Importance factor
Vibrationdata
Parameters | Meaning | Units | Notes
SDS | Design spectral acceleration, short periods | G | = 2/3 × SMS
SD1 | Design spectral acceleration, 1 sec | G | = 2/3 × SM1
Tₛ | Transition period | sec | = SD1 / SDS
T₀ | 0.2 × Tₛ | sec | Defines lower bound period
TL | Long-period transition | sec | Used in design spectrum shape
But:
  Adjusted for structure type
  May include impulsive + convective components (tanks)
SMS & SM1 are design spectral values

## Slide 17
Dynamic Behavior Differences
Nonbuilding structures often exhibit:
  Flexible appendages
  Fluid-structure interaction
  Sloshing effects
  Higher modes significant
  Standard Equivalent Force (ELF) may be inadequate
Vibrationdata

## Slide 18
Example
The subscript "p" on the following factors simply denotes they are component-specific values
Vibrationdata
Condition | aₚ | Rₚ | Ω₀ₚ
Mounted directly (rigid) — equipment period Tₐ ≤ 0.06s | 1.0 | 2.5 | 2.0
Vibration isolated — flexible mounting | 2.5 | 2.5 | 2.0
Flexibly mounted / on a supporting frame (as shown in your image) | 2.5 | 2.5 | 2.0

## Slide 19
Parameter | Value | Source
SDS | 1.24g | USGS ASCE 7-22, Los Angeles, Site Class D
Ip | 1.5 | Essential/ hazardous facility
Rp | 2.5 | ASCE 7-22
SDC | D | Given
h (floor-to-top height of structure) | 8 ft | Given
Height of CG above base | 36 inch | Given
Wp | 5000 lbm (5 kips) | Given
Equipment on Supporting Beam Frame

## Slide 20
Example
Height amplification factor
z = h for this sample problem
Component seismic force
Per ASCE 7-22 §13.3.1, the factor a₁ depends on the number of stories of the supporting structure:
  a₁ = 2.5 for a one-story structure
  a₁ = 2.0 for a two-or-more story structure

## Slide 21
Example
Vibrationdata

## Slide 22
Example
Vibrationdata