## Slide 1
SEISMIC DESIGN OF
Architectural Glazing
Story Drift, Glass Fallout & Component Forces
Displacement limits across three orthogonal axes — U.S. (ASCE 7 / AAMA) and European (EN 1998-1) practice
Tom Irvine
Vibration & Structural Dynamics • vibrationdata
1
vibrationdata

## Slide 2
ORIENTATION
Three Orthogonal Axes of Demand
Glazing in an earthquake sees demand in all three axes, but the failure mechanisms — and the governing code checks — are different in each.
DRIFT
In-Plane (X)
Interstory drift / racking
Frame shears as floors displace laterally relative to one another. Glass must ride out the drift or fall out. THE dominant glazing concern.
FORCE
Out-of-Plane (Y)
Inertial component force
Panel mass accelerates normal to its plane. An inertial-force problem governing anchorage and structural-silicone bite.
COMBO
Vertical (Z)
Vertical seismic effect
Secondary for glass itself; enters load combinations and governs horizontal facade members (sunshades, spandrels, canopies).
2
vibrationdata

## Slide 3
AXIS 1 · IN-PLANE — U.S. PRACTICE
Design Story Drift (ASCE 7, Ch. 12)
The elastic analysis runs on reduced design forces; the deflection amplification factor restores the expected inelastic displacement.
elastic deflection from analysis
deflection amplification factor of the SFRS
seismic importance factor
design story drift over the story
SFRS = Seismic Force-Resisting System
ALLOWABLE STORY DRIFT Δa
ASCE 7 Table 12.12-1 — varies with structure type & Risk Category
0.025 hsx
Most structures, Risk Cat. I–II
0.020 hsx
Risk Category III
0.015 hsx
Risk Category IV
0.010 hsx
Masonry shear-wall (cantilever)
Δ ≤ Δa ( hsx = story height )
3
vibrationdata

## Slide 4
AXIS 1 · IN-PLANE — U.S. PRACTICE
The Glass Fallout Check (ASCE 7 §13.5.9)
Glass is an architectural component. It must demonstrate a fallout drift that exceeds the design displacement demand — with an explicit 25% margin.
Δfallout = drift causing glass fallout (AAMA 501.6 test)
Dp = relative seismic displacement the glass must accommodate
…OR SATISFY AN EXEMPTION
1 · Clearance exemption — glass floats within its frame
= pane height
= pane width
= vertical edge clearance
= horizontal edge clearance
2 · Fully tempered monolithic glass
Risk Cat. I–III, ≤ 10 ft above a walking surface
3 · Laminated annealed/heat-strengthened glass
Interlayer ≥ 0.030 in., mechanically captured in the glazing pocket
4
vibrationdata

## Slide 5
AXIS 1 · IN-PLANE — U.S. PRACTICE
Relative Seismic Displacement, Dp
Dp is the displacement demand the glazing must absorb — the relative movement between its two attachment points. ASCE 7 §13.3.2 defines it; for glazing the value is the design drift over the supporting story.
GENERAL — TWO POINTS ON THE SAME STRUCTURE
deflection at higher attachment, level x
deflection at lower attachment, level y
BOUNDED BY THE ALLOWABLE DRIFT
FOR A ONE-STORY PANEL
A glazing unit spanning a single story takes Dp as the design interstory drift over that story height:
Then check: Δfallout ≥ 1.25 Ie Dp
…or the clearance exemption Dclear ≥ 1.25 Dp from the previous slide.
hsx = story height • (z − x) spans one story for a typical glazed unit, so Dp reduces to the interstory drift.
5
vibrationdata

## Slide 6
AXIS 1 · IN-PLANE — QUALIFICATION
Racking Test Methods (AAMA)
AAMA 501.4
Serviceability at design drift
Static interstory-drift test for curtain wall & storefront under seismic and wind drift. Demonstrates the system survives the design-level event intact — no glass breakage, no gasket disengagement, no permanent frame damage.
Lower bar: design-level event
AAMA 501.6
Drift causing glass fallout
Crescendo (increasing-amplitude) racking of a full-scale specimen until glass falls out. Yields the empirical Δfallout fed into the §13.5.9 inequality. (Despite the legacy 'Dynamic' title, it is a stepped-displacement protocol.)
Failure threshold: Δfallout
501.4 proves the system endures the design drift; 501.6 finds the drift at which it catastrophically fails. The code fallout check uses the 501.6 result against the 1.25-amplified demand.
6
vibrationdata

## Slide 7
AXIS 2 · OUT-OF-PLANE — U.S. PRACTICE
Component Force (ASCE 7 §13.3.1)
Not a drift problem — an inertial one. The panel and frame must resist their own mass accelerating normal to the facade. Governs anchorage and structural-silicone bite.
component amplification factor
component response modification factor
short-period design spectral acceleration
component operating weight
component importance factor
attachment height / roof height
THE (1 + 2z/h) TERM
Floor accelerations amplify up the building. A component at the roof (z/h = 1) sees a factor of 3 — three times the base demand.
×1
z/h=0
×2
z/h=.5
×3
z/h=1
7
vibrationdata

## Slide 8
AXIS 3 · VERTICAL — U.S. PRACTICE
Vertical Seismic Load Effect
Rarely controls the glass or its in-plane framing — but it rides through the load combinations and governs horizontally-spanning facade members.
vertical seismic load effect
short-period design spectral acceleration
dead load
WHERE IT MATTERS FOR FACADES
Sunshades & light shelves
cantilevered horizontal members carry direct vertical demand
Spandrel & canopy framing
long horizontal spans hung off the facade
Connections
vertical demand combines with horizontal at anchors
8
vibrationdata

## Slide 9
AXIS 1 · IN-PLANE — EUROPEAN PRACTICE
EN 1998-1 (Eurocode 8) Drift Limits
Eurocode 8 ties the interstory-drift limit to how the non-structural elements are attached. The damage-limitation check uses the 'frequent' (serviceability) earthquake.
design interstory drift
reduction factor — 0.5 (class I–II), 0.4 (III–IV)
story height
0.5 %
Brittle non-structural elements
fixed to the structure (typical glazing)
0.75 %
Ductile non-structural elements
fixed to the structure
1.0 %
Isolated / decoupled elements
not interfering with deformations
Limit applies to dr·ν, expressed as a drift ratio (% of story height). For ordinary glazing fixed to the frame, the 0.5% brittle limit usually governs.
9
vibrationdata

## Slide 10
AXIS 2 · OUT-OF-PLANE — EUROPEAN PRACTICE
EN 1998-1 Non-Structural Element Force
Eurocode 8 §4.3.5 applies a horizontal force Fa at the element's center of mass. The seismic coefficient Sa carries the same up-the-height amplification as ASCE 7.
(lower bound)
seismic coefficient for the element
weight of the element
importance factor of the element
behaviour factor of the element (1.0 or 2.0)
ratio ag / g (design ground accel.)
soil factor
element / structure fundamental period
element height / building height
qa = 2.0 for facade panels & glazing on the building face; the (1 + z/H) term mirrors ASCE 7's height amplification.
10
vibrationdata

## Slide 11
SIDE BY SIDE (1 OF 2)
U.S. vs. European Framework
Aspect | U.S. (ASCE 7 / AAMA) | Europe (EN 1998-1)
Governing document | ASCE 7 Ch. 12 (drift) & Ch. 13 (components) | EN 1998-1 §4.3.4 (drift) & §4.3.5 (elements)
In-plane limit basis | Δa per Table 12.12-1 (0.010–0.025 hsx) | Drift ratio by attachment: 0.5 / 0.75 / 1.0 %
Reference event | Design earthquake (with Cd amplification) | 'Frequent' earthquake (ν = 0.5 / 0.4)
Glass fallout check | Explicit, test-verified margin (AAMA 501.6) | No equivalent explicit fallout inequality
Qualification test | AAMA 501.4 (serviceability) & 501.6 (fallout) | Product standard EN 13830; no fallout test
Vertical effect basis | Always in load combinations | Only where vertical spectrum avg > 0.25 g
Governing equations compared on the next slide. Key divergence: the U.S. mandates a test-verified fallout margin; Eurocode 8 controls glazing via the drift-ratio limit.
11
vibrationdata

## Slide 12
SIDE BY SIDE (2 OF 2)
Governing Equations Compared
U.S. (ASCE 7 / AAMA)
Europe (EN 1998-1)
Glass fallout
check
No equivalent explicit
fallout inequality
Out-of-plane
force
Height
amplification
Vertical
effect
Vertical elastic spectrum
where avg > 0.25 g
Both frameworks amplify out-of-plane demand up the building height; only ASCE 7 ties glass retention to a physical fallout test.
12
vibrationdata

## Slide 13
PRACTICE
Design-Check Workflow
1
Extract design drift
Get interstory drift Δ from analysis, scaled Cd/Ie (ASCE) or dr·ν (EC8).
2
Compute Dp
Relative seismic displacement the glazing must accommodate over the story.
3
Fallout or clearance
Verify Δfallout ≥ 1.25 Ie Dp (501.6 test) OR clearance Dclear ≥ 1.25 Dp.
4
Out-of-plane force
Check Fp (or Fa) for framing anchorage & structural-silicone bite.
5
Vertical in combos
Carry Ev through load combinations for horizontal facade members.
Same logical flow on both sides of the Atlantic — only the coefficients and the explicit fallout test differ.
13
vibrationdata

## Slide 14
REFERENCE
Standards & Key Takeaways
TAKEAWAYS
In-plane drift is the dominant glazing concern
the glass must ride out racking or fall out
The 1.25 factor is the explicit U.S. safety margin
tested fallout drift must beat demand by 25%
Out-of-plane is an inertial-force problem
both codes amplify demand up the height
EC8 controls glazing via the drift-ratio limit
0.5% brittle limit typically governs glazing
Confirm the governing code edition before citing
ASCE 7-22 reformulated the component-force method
UNITED STATES
ASCE 7 Minimum Design Loads & Associated Criteria — Ch. 12 (drift), Ch. 13 (components)
AAMA 501.4 Static drift serviceability test method
AAMA 501.6 Seismic drift causing glass fallout
ASTM E2026 / E1300 Building performance & glass design
EUROPE
EN 1998-1 Eurocode 8 — §4.3.4 drift limitation, §4.3.5 non-structural elements
EN 13830 Curtain walling — product standard
EN 12152 / 12154 Air permeability & watertightness of curtain walls
EN 16612 Lateral load resistance of glass panes
14
vibrationdata