## Slide 1
Vibrationdata
ASCE 7-22 Seismic Anchor Bolt Design
Revision A
By Tom Irvine
1

## Slide 2
Vibrationdata
Overview
2
Seismic anchor bolt design for ground-mounted equipment and nonstructural components
Governing codes:
  ASCE 7-22 Chapters 11–13: Seismic design forces and load combinations
  ACI 318-19 Chapter 17: Concrete anchor strength — all failure modes
  ICC-ES AC193 / AC308: Qualification of post-installed mechanical and adhesive anchors
This deck covers:
  Site seismic hazard parameters ( , Seismic Design Category)
  Chapter 13 nonstructural component force equation and parameter selection
  Overturning analysis — combined tension and shear demands on anchors
  ACI 318-19 failure modes and interaction check
  SDC D ductility requirements and post-installed anchor considerations
  Worked example: electronics rack at Vandenberg SFB ( = 0.792g, SDC D)

## Slide 3
Vibrationdata
Regulatory Framework
3
ASCE 7-22 is the primary loading standard adopted by IBC 2021
  Chapter 11: Seismic ground motion values and site classification
  Chapter 12: Seismic design requirements for building structures
  Chapter 13: Seismic design of nonstructural components
  Chapter 15: Nonbuilding structures (equipment skids, tanks, frames)
ACI 318-19 Chapter 17 governs all anchor design to concrete
  Steel failure modes: tension fracture (§17.6.1), shear fracture (§17.7.1)
  Concrete failure modes: breakout (§17.6.2), pullout (§17.6.3), pryout (§17.7.3)
  Combined tension + shear interaction check (§17.8)
Post-installed anchor qualification standards:
  ICC-ES AC193: mechanical (expansion) anchors — Seismic Category 1 required for SDC C–F
  ICC-ES AC308: adhesive anchors — temperature and sustained-load knockdown apply

## Slide 4
Vibrationdata
Site Seismic Hazard — ASCE 7-22 §11.4
4
MCER spectral accelerations from USGS Seismic Hazard Maps:
  = short-period MCER (2% in 50 yr)
  = 1-second MCER
Site coefficients (Tables 11.4-1 and 11.4-2) for Site Classes A–F:
  applied to ; applied to
  Site Class D (stiff soil) is the default when subsurface data are unavailable
MCER adjusted for site class:
Design-level spectral accelerations (2/3 of MCER):
  and
Seismic Design Category (SDC) determined from , , and Risk Category (Tables 11.6-1/2)

## Slide 5
Vibrationdata
Site Seismic Hazard — ASCE 7-22 §11.4
4
SDC from (Risk Cat. I/II):
Range | SDC
< 0.167g | A
0.167 – 0.33g | B
0.33 – 0.50g | C
> 0.50g | D
 | SDC
< 0.167g | A
0.167 – 0.33g | B
0.33 – 0.50g | C
> 0.50g | D
Vandenberg SFB example:
= 0.792g
= 0.390g
Site Class D
SDC D (Risk Cat. I/II/III)
Always use USGS Design Maps tool for site lat/lon

## Slide 6
Vibrationdata
Chapter 13 — Nonstructural Component Force
5
Symbol | Description | Typical Values
 | Component amplification factor | 1.0 (rigid, > 16.7 Hz) or 2.5 (flexible)
 | Design spectral acc., short period | Site-specific from USGS
 | Component operating weight (lbf) | Use maximum operating weight
 | Height ratio (attachment / avg. roof) | 0 at grade; 1.0 at roof level
 | Response modification factor | 1.5 to 12.0 — see Table 13.5-1
 | Component importance factor | 1.0 (standard) or 1.5 (essential)
Symbol | Description | Typical Values
 | Component amplification factor | 
 | Design spectral acc., short period | Site-specific from USGS
 | Component operating weight (lbf) | Use maximum operating weight
 | Height ratio (attachment / avg. roof) | 0 at grade; 1.0 at roof level
 | Response modification factor | 1.5 to 12.0 — see Table 13.5-1
 | Component importance factor | 1.0 (standard) or 1.5 (essential)

## Slide 7
Vibrationdata
Chapter 13 — Nonstructural Component Force (cont)
5
Limits (Eqs. 13.3-3 and 13.3-4):
(lower bound — must not be less than this)
(upper bound — governs at roof with flexible component)
Vertical seismic: (§12.4.2) — applied upward for maximum anchor tension

## Slide 8
Vibrationdata
Anchor System Design Strengths for Tension, ACI Notation
16
= design steel strength of the anchor in tension
  Failure mode: anchor steel yields or fractures
= design concrete breakout strength in tension
  Failure mode: concrete cone pulls out of the base material
= design pullout strength in tension
  Failure mode: anchor head, hook, or bearing surface pulls out of the concrete

## Slide 9
Vibrationdata
Multiaxial Anchor Stress — Combined Tension and Shear
7
A single seismic event produces simultaneous lateral force AND overturning moment
The lateral force acts at the component CG, generating:
  Base shear → resolved into shear () on every anchor bolt
  Overturning moment → resolved into tension () on the windward anchors
Both and reach their peak at the same instant — unlike pyrotechnic shock, seismic is a static-equivalent load; axes are not independent
The anchor cross-section therefore carries combined stress:
  Tensile stress in the bolt threaded section
  Shear stress in the bolt shank
These stresses interact — the combined state reduces capacity below each uniaxial limit
Vertical seismic adds an upward force component that further increases net anchor tension
Equipment
CG
Inertial Force
(tension)
(compression)
(shear, all anchors)
Anchor stress state:
(tension)
(shear)
Both act simultaneously
Interaction check required

## Slide 10
Vibrationdata
Overturning Analysis — Equilibrium Equations
8
Overturning moment about the controlling bolt pattern axis:
Resultant tension in the windward bolt group (moment equilibrium about compression side):
Tension demand per anchor (including upward vertical seismic):
Shear demand per anchor (uniform distribution among all n anchors):
d = half-span of anchor pattern perpendicular to overturning axis (in)
= number of anchors in the tension group; n = total anchors
Use the shorter bolt pattern span — it produces the larger

## Slide 11
Vibrationdata
Component Parameters — ASCE 7-22 Table 13.5-1 (Selected)
6
Component Type |  |  | Notes
Electronics / communications racks — braced | 1.0 | 2.5 | Rigid if > 16.7 Hz; else use 2.5
Electronics / communications racks — unbraced | 2.5 | 2.5 | Always treated as flexible
Mechanical equipment — general | 1.0 | 2.5 | Rigid attachment assumed
Mechanical equipment on vibration isolators | 2.5 | 2.5 | Check isolator type and stiffness
Storage racks, high-piled storage | 2.5 | 4.0 | Table 13.5-1, item 5
Equipment on seismic isolators | 2.5 | 2.5 | Isolated — inherently flexible
Architectural parapets and appendages | 2.5 | 2.5 | Always flexible; high risk
Component Type |  |  | Notes
Electronics / communications racks — braced | 1.0 | 2.5 | 
Electronics / communications racks — unbraced | 2.5 | 2.5 | Always treated as flexible
Mechanical equipment — general | 1.0 | 2.5 | Rigid attachment assumed
Mechanical equipment on vibration isolators | 2.5 | 2.5 | Check isolator type and stiffness
Storage racks, high-piled storage | 2.5 | 4.0 | Table 13.5-1, item 5
Equipment on seismic isolators | 2.5 | 2.5 | Isolated — inherently flexible
Architectural parapets and appendages | 2.5 | 2.5 | Always flexible; high risk
= 1.5 for components in Risk Category IV, components whose failure poses significant hazard (toxic storage), or life-safety systems
= 1.0 for all other components
When the component natural frequency is not known, assume = 2.5 (conservative)

## Slide 12
ACI 318-19 Chapter 17 — Concrete Anchor Failure Modes
Vibrationdata
Variable Definitions (1 of 2)
Symbol | Definition | Units
 | Nominal steel tensile strength of anchor | lbf or kip
 | Effective cross-sectional stress area of anchor | in²
 | Specified ultimate tensile strength of anchor steel | psi or ksi
 | Nominal concrete breakout strength of an anchor group in tension | lbf or kip
 | Projected concrete failure area of anchor group (actual) | in²
 | Projected concrete failure area of a single anchor without edge effects | in²
 | Modification factor for eccentrically loaded anchor groups in tension | –
 | Modification factor for edge distance effects on breakout strength | –
 | Modification factor for cracking at service loads (breakout) | –
 | Modification factor for splitting failure (post-installed anchors) | –
 | Basic concrete breakout strength of a single anchor in tension | lbf or kip
Symbol | Definition | Units
 | Nominal steel tensile strength of anchor | lbf or kip
 | Effective cross-sectional stress area of anchor | in²
 | Specified ultimate tensile strength of anchor steel | psi or ksi
 | Nominal concrete breakout strength of an anchor group in tension | lbf or kip
 | Projected concrete failure area of anchor group (actual) | in²
 | Projected concrete failure area of a single anchor without edge effects | in²
 | Modification factor for eccentrically loaded anchor groups in tension | –
 | Modification factor for edge distance effects on breakout strength | –
 | Modification factor for cracking at service loads (breakout) | –
 | Modification factor for splitting failure (post-installed anchors) | –
 | Basic concrete breakout strength of a single anchor in tension | lbf or kip
10

## Slide 13
ACI 318-19 Chapter 17 — Concrete Anchor Failure Modes
Vibrationdata
Variable Definitions (2 of 2)
Symbol | Definition | Units
 | Effective embedment depth of anchor | in
 | Nominal pullout strength of a single anchor in tension | lbf or kip
 | Net bearing area of anchor head, nut, or washer | in²
 | Specified compressive strength of concrete | psi or ksi
 | Modification factor for cracking at service loads (pullout) | –
 | Nominal side-face blowout strength of a single headed anchor | lbf or kip
 | Distance from center of anchor shaft to edge of concrete in direction of load | in
 | Strength reduction factor — steel tensile failure (ductile) | 0.75
 | Strength reduction factor — concrete breakout in tension | 0.70
 | Strength reduction factor — pullout / pullthrough | 0.70
 | Strength reduction factor — side-face blowout | 0.70
Symbol | Definition | Units
 | Effective embedment depth of anchor | in
 | Nominal pullout strength of a single anchor in tension | lbf or kip
 | Net bearing area of anchor head, nut, or washer | in²
 | Specified compressive strength of concrete | psi or ksi
 | Modification factor for cracking at service loads (pullout) | –
 | Nominal side-face blowout strength of a single headed anchor | lbf or kip
 | Distance from center of anchor shaft to edge of concrete in direction of load | in
 | Strength reduction factor — steel tensile failure (ductile) | 0.75
 | Strength reduction factor — concrete breakout in tension | 0.70
 | Strength reduction factor — pullout / pullthrough | 0.70
 | Strength reduction factor — side-face blowout | 0.70
11

## Slide 14
Vibrationdata
ACI 318-19 Chapter 17 — Concrete Anchor Failure Modes
9
Tension failure modes — all must be checked:
  Steel tensile fracture
  (ductile, preferred governing mode)
  Concrete breakout
  (subscript N for tension omitted for brevity)
  Pullout / pullthrough
  (cast-in bolt head bearing)
  Side-face blowout (near-edge, deep embedment)

## Slide 15
Vibrationdata
ACI 318-19 Chapter 17 — Concrete Anchor Failure Modes
9
Shear failure modes — all must be checked:
  Steel shear fracture
  Concrete pryout
  Concrete breakout in shear
  Governs when anchors are near a free edge in the shear direction
Design strength = × (minimum of all applicable nominal strengths)
The weakest failure mode governs — compute all, use minimum

## Slide 16
Vibrationdata
Combined Tension and Shear — ACI 318-19 §17.8
10
ACI 318-19 §17.8.3 — linear interaction for combined tension + shear:
Two-check simplification (§17.8.3):
  If → check shear only:
  If → check tension only:

## Slide 17
Vibrationdata
Combined Tension and Shear — ACI 318-19 §17.8 (cont)
10
Design verification sequence:
  1. Compute and per anchor from overturning analysis
  2. Compute
  3. Compute
  4. Apply interaction check:
  5. Verify SDC ductility path per ACI §17.10
Note: the 1.2 upper limit (vs. 1.0 for fully conservative interaction) accounts for the linear equation being slightly over-conservative relative to test data
Both and act simultaneously — axis independence does not apply for static-equivalent seismic loading

## Slide 18
Vibrationdata
Concrete Breakout in Tension — ACI 318-19 §17.6.2
11
Basic single-anchor breakout (Eq. 17.6.2.2a, in-lbf units):
Group breakout (Eq. 17.6.2.1b) with five modification factors:

## Slide 19
Vibrationdata
Concrete Breakout in Tension — ACI 318-19 §17.6.2 (cont)
11
Factor | Meaning | Value
 | Projected cone area ratio. | < 1 when edge or spacing limits area
 | Eccentricity. | ≤ 1.0 — reduces for non-uniform loading
 | Edge distance. | = 0.7 + 0.3 c_a,min / (1.5 h_ef) otherwise
 | Cracking. 1.25 uncracked / 1.0 cracked | Use 1.0 (cracked) at SDC D
 | Splitting (post-installed). 1.0 for cast-in | ≥ c_a,min / c_ac for post-installed
Factor | Meaning | Value
 |  | < 1 when edge or spacing limits area
 |  | ≤ 1.0 — reduces for non-uniform loading
 |  | = 0.7 + 0.3 c_a,min / (1.5 h_ef) otherwise
 | Cracking. 1.25 uncracked / 1.0 cracked | Use 1.0 (cracked) at SDC D
 | Splitting (post-installed). 1.0 for cast-in | ≥ c_a,min / c_ac for post-installed
is the effective eccentricity of the applied tensile load relative to the centroid of the anchor group
Check edge distance for all anchors: if factor reduces breakout capacity

## Slide 20
Vibrationdata
Worked Example — Problem Description
12
Component: electronics rack, = 500 lbf (operating)
Rack dimensions: 24" W × 36" D × 72" H
CG height above floor: = 36 in
Attachment: grade-level concrete slab (z = 0 ft)
Building height: h = 14 ft
Site: Vandenberg SFB
  = 0.792g, = 0.390g
  Site Class D, SDC D
Component parameters:
  = 2.5 (flexible — racking mode below 16.7 Hz)
  = 2.5 (braced rack, ASCE 7 Table 13.5-1)
  = 1.5 (essential facility)
Anchor configuration:
  4 anchors, 1/2" dia., ASTM F1554 Grade 55 cast-in rods
  Pattern: 12" (X) × 18" (Y) rectangular
  Embedment = 6.0 in; = 4000 psi NW concrete
Electronics Rack
CG = 36"
Concrete slab ( = 4000 psi)
Tension ()
Compression
(shear)
Plan view — 12" × 18" pattern
Inertial Force

## Slide 21
Vibrationdata
Worked Example — Force and Anchor Demands
13
Seismic design force (ASCE 7-22 Eq. 13.3-1):
Max check:
Vertical seismic and overturning ( controlling Y-axis, ):
Both and act on the same anchor simultaneously — the interaction check must account for the combined multiaxial stress state

## Slide 22
Vibrationdata
Worked Example — ACI 318-19 Anchor Capacity
14
Anchor: ½" ASTM F1554 Gr. 55 cast-in,
Failure Mode | Nominal Capacity | φ |  | Governs?
Steel tensile ( ) | 0.75 × 0.142 × 75 = 8.0 kips | 0.75 | 6.0 kips | No
Breakout ( ) | Group ≈ 74 kips → 13 kips/anchor | 0.70 | 13 kips/anchor | No
Pullout ( ) |  | 0.70 | 5.2 kips | YES — tension
Steel shear ( ) | 0.6 × 0.142 × 75 = 6.4 kips | 0.65 | 4.1 kips | YES — shear
Pryout ( ) | 2.0 × 74 = 148 kips (group) | 0.70 | 103.6 kips (group) | No
Failure Mode | Nominal Capacity | φ |  | Governs?
 | 0.75 × 0.142 × 75 = 8.0 kips | 0.75 | 6.0 kips | No
 | Group ≈ 74 kips → 13 kips/anchor | 0.70 | 13 kips/anchor | No
 |  | 0.70 | 5.2 kips | YES — tension
 | 0.6 × 0.142 × 75 = 6.4 kips | 0.65 | 4.1 kips | YES — shear
 | 2.0 × 74 = 148 kips (group) | 0.70 | 103.6 kips (group) | No
Controlling capacities: (pullout) , (steel shear)

## Slide 23
Vibrationdata
Worked Example — ACI 318-19 Anchor Capacity (cont)
14
Interaction ratio = 0.156 — well below 1.2; the design has substantial reserve capacity
Pullout governs over breakout because the anchor group is far from slab edges
Steel ductile tensile failure () governs over pullout capacity (5.2) — check SDC D ductility

## Slide 24
Vibrationdata
SDC D Special Requirements — ACI 318-19 §17.10
15
At SDC C through F, the anchor connection must satisfy one of three ductility paths:
Option A — Ductile Steel Governs (preferred)
Steel yields before any brittle concrete failure — most predictable energy dissipation
Worked example: kips < = 13 kips/anchor → confirmed ✓
Option B — Group Ductility
Concrete group capacity must exceed steel yield force by a ductility factor
Less common for equipment anchorage; requires careful calculation
Option C — Overstrength (Ω₀ = 2.0)
Design anchors for where (ASCE 7-22 Table 12.2-1)
Required when ductility cannot be demonstrated (non-ductile post-installed, breakout governs)
Doubles the design demand — often drives redesign to cast-in or larger-diameter rods
Worked example satisfies Option A — no overstrength factor needed for this cast-in anchor configuration

## Slide 25
Vibrationdata
Post-Installed Anchors
16
Mechanical (expansion) anchors — ICC-ES AC193:
  Torque-controlled or displacement-controlled types
  Must achieve Seismic Category 1 for SDC C–F
  Category 1 = tested in cracked concrete with seismic cyclic shear loading
  Examples: Hilti Kwik Bolt TZ, Simpson Strong-Bolt
Adhesive (chemical) anchors — ICC-ES AC308:
  Temperature knockdown factor for elevated-temperature service
  Sustained tensile load reduction factor must be applied
  Must achieve Category 1 (cracked concrete) for SDC C–F
  Examples: Hilti HIT-RE 500, Simpson SET-XP

## Slide 26
Vibrationdata
Post-Installed Anchors
16
Cracked concrete requirement:
  At SDC D, concrete is assumed cracked — use (not 1.25)
  Post-installed: apply and reduction factors per ICC-ES report
SDC D caution — overstrength requirement:
  If concrete breakout governs (not steel fracture), Option A ductility fails
  Must use Option C: design anchors for
  This can double demand — often the design must switch to cast-in anchors or increase rod diameter
API practice note:
  Always verify the specific anchor's ICC-ES report seismic category before finalizing design
  Some anchors are listed Category 2 only — not permitted for SDC C–F under §17.10.5.3

## Slide 27
Vibrationdata
Worked Example — Summary of Results
17
Design Step | Result | Code Reference | Status
Site hazard | 0.792g, SDC D | ASCE 7-22 §11.4 | ✓
Seismic force (Eq. 13.3-1) | 238 lbf | §13.3.1 | ✓ Controls
limits | 178 / 950 lbf | Eqs. 13.3-3/4 | ✓ In range
Vertical seismic | 79.2 lbf (upward) | §12.4.2 | ✓ Applied
Overturning | 8,568 lbf·in | Statics | ✓
Anchor tension | 734 lbf | Combined loading | ✓
Anchor shear | 59.5 lbf | Uniform distribution | ✓
(pullout governs) | 5,200 lbf | ACI 318-19 §17.6.3 | ✓
(steel shear governs) | 4,100 lbf | ACI 318-19 §17.7.1 | ✓
Interaction ratio | 0.156 ≤ 1.2 | ACI 318-19 §17.8.3 | ✓ PASS
SDC D ductility (Option A) | confirmed | ACI 318-19 §17.10 | ✓ PASS
Design Step | Result | Code Reference | Status
 | 0.792g, SDC D | ASCE 7-22 §11.4 | ✓
 | 238 lbf | §13.3.1 | ✓ Controls
 | 178 / 950 lbf | Eqs. 13.3-3/4 | ✓ In range
 | 79.2 lbf (upward) | §12.4.2 | ✓ Applied
 | 8,568 lbf·in | Statics | ✓
 | 734 lbf | Combined loading | ✓
 | 59.5 lbf | Uniform distribution | ✓
 | 5,200 lbf | ACI 318-19 §17.6.3 | ✓
 | 4,100 lbf | ACI 318-19 §17.7.1 | ✓
Interaction ratio | 0.156 ≤ 1.2 | ACI 318-19 §17.8.3 | ✓ PASS
SDC D ductility (Option A) |  | ACI 318-19 §17.10 | ✓ PASS

## Slide 28
Vibrationdata
Worked Example — Summary of Results (cont)
17
The controlling failure mode is pullout (tension) and steel fracture (shear) — both are non-brittle or ductile for cast-in anchors
The combined interaction ratio of 0.156 indicates the ½" anchors are substantially adequate; a smaller rod diameter could be explored if construction permits

## Slide 29
Vibrationdata
Design Checklist — ASCE 7-22 Seismic Anchor Bolt Analysis
18
Obtain and from USGS Design Maps for the specific site latitude/longitude
Confirm Site Class from geotechnical report; default to Site Class D if data unavailable
Determine Risk Category (I–IV) and SDC from ASCE 7-22 Tables 11.6-1/2
Select and from Tables 13.5-1/2 for the specific component type
Set = 1.5 for essential, hazardous, or life-safety components
Compute (Eq. 13.3-1) and verify and limits
Apply vertical seismic to anchor tension demands

## Slide 30
Vibrationdata
Design Checklist — ASCE 7-22 Seismic Anchor Bolt Analysis
18
Perform overturning moment analysis; use shortest bolt pattern span for maximum tension
Compute and per anchor — both must be treated simultaneously
Calculate all ACI 318-19 §17 failure mode capacities:
Apply §17.8.3 interaction check:
Verify SDC D ductility path per ACI §17.10 (Option A preferred; Option )
For post-installed anchors: confirm ICC-ES seismic category; apply (cracked)
Check edge distance: if apply reduction to breakout capacity